# POWER THROUGH RELAY MODULES

## General

### The modules shall be EC21 Power Through Relay modules as manufactured by Vari-Lite, LLC.

### Dimmer modules shall be available with or without reporting options and shall comprise of one of the following power ratings:

#### 16A  with 250uS rise times for 230 Volt operations

#### 16A  with 400uS rise times for 230 Volt operations

#### 25A  with 250uS rise times for 230 Volt operations

#### 25A  with 400uS rise times for 230 Volt operations

### Each EC21 Power Through Relay modules shall be designed for complete flexibility of choice for dimmed, non-dim or bypass operation on each branch circuit.  A single Power Through Relay module shall provide:

#### Two (2) three position selector switches

#### Two (2) RCBO protective devices with a C class characteristic breaker

#### Two (2) dimmed outputs with rise times for 230Volt applications

#### Two (2) air gap relay switched outputs controlled by DMX

### The module may be configured to operate as two dimmers, two relays, two direct power (bypass) feeds or any combination of relay/dimmer/bypass feed from the face of each Power Thru Module.  Any single circuit may be set to the required mode for the dimmer using a switch on the front of the module.  Remote mode switching from the console shall expressly not be an option to avoid inadvertent dimming of a Solid State Light or other devices.

## Electrical

### Each Power Through Relay module shall contain the following components

#### circuit breakers

#### SCR solid-state dimming modules

#### toroid filters

#### power and control connectors

#### 230VAC remotely controllable mechanically air gap relays

#### Two 3 position mode selector switches

### The dimmer modules shall be designed using advanced, state-of-the-art components. The dimmer module shall be capable of "hot patching" cold, incandescent loads up to its full rated capacity without malfunction with the control signal at full ON.

### The dimmer modules shall be fully plug-in and factory wired. Dimmer modules shall be of rugged and heavy-duty construction enclosed by a formed aluminum chassis.

### Power and signal pins shall be recessed in a self-aligning housing to avoid handling, storage, and insertion damage.

### A contoured handle shall be provided for ease of insertion and withdrawal.

### All chassis parts, except heat sinks, shall be properly treated, primed and finished in fine texture, scratch resistant, coating.  Modules constructed of molded plastic for structural support shall not be acceptable.  Each module shall be labeled with the Philips Strand Lighting logo and rating.

### Dimmer modules shall be keyed so that dimmer modules of greater capacity shall not be interchangeable.

### Standard dimmer electronics shall be completely solid state. They shall utilize two silicon controlled rectifiers in a back-to-back electrical configuration. The full load of the circuit is to be carried and controlled by the silicon controlled rectifiers.

### Each 230 volt dimmer shall be protected by a RCBO breaker of the appropriate current rating and 6kA fault rating mounted on the face plate of the dimmer module, so that the trip current is not affected by ambient or rack temperature.  The circuit breaker shall be with a C class characteristic rated for tungsten loads and shall disconnect the power to the dimmer module before damage can be done to the dimmer power components.

### Dimmer modules shall be marked as CE devices.

## Dimmer Module Power Devices.

### SSR power devices shall be encapsulated, epoxy filled high impact plastic cases with optically isolated firing circuits, control circuitry, and two silicon controlled rectifiers (SCR's).

### There shall be a minimum of 4,000 volts RMS of isolation between the AC line and the control lines of the SCR.

### The SCR shall be in an industry standard format that is easily field replaceable, without removing any other electrical or electronic devices.

## SCR Power Device Filtering.

### Each SCR power device dimmer module shall have an integral inductive filter to reduce the rate of current rise time resulting from the SSR switching on. The filter shall limit objectionable harmonics, reduce lamp filament sing and limit the radio frequency interference on line and load conductors.

### Basic Rise 230 volt dimmers shall have a rise time of not less than 250 microseconds measured at 90 degrees conduction angle from 10% to 90% of output wave form with dimmer operating at maximum load.

### High Rise 230 volt dimmers shall have a rise time of not less than 400 microseconds measured at 90 degrees conduction angle from 10% to 90% of output wave form with dimmer operating at maximum load.

## Approved Manufacturer and Products.

Dimmer racks, modules and control electronics shall be Strand EC21 Advanced Technology dimmer racks.